“dsconfig”, a Tango configuration tool
Johan Forsberg
Tango meeting 22-06-30

---
Rubrik Calibri Bold 32-36 p
What is dsconfig?
A command line tool that reads a configuration from a file and applies it to an existing Tango control system.
Depends on PyTango
Defines a JSON file format
https://gitlab.com/MaxIV/lib-maxiv-dsconfig

---
JSON file format
"servers": {
        "some-server/instance": {
        "SomeDeviceClass": {
        "some/device/1": {
        "properties": {
        "someImportantProperty": [
        "foo",
        "bar"
        ],
        "otherProperty": ["7"]
        },
        "attribute_properties": {
        "anAttribute": {
        "min_value": ["-5"],
        "unit": ["mV"]
        }
        }
        “some/device/2”: { ...

---
How it works
1. Read and validate the JSON file
2. “Dump” the relevant parts of the Tango database
3. Compare the two configurations
    → If there is no difference, we are already done!
4. Display the “diff” to the user
    → If the “--write” flag was not added, stop here.
5. Add/remove/change in the database what is needed for the user supplied configuration to be “true”.

---
What is the point?
Tango DB is a “moving target”; automated configuration may overwrite important manual changes
Applying configuration with deployment tools like Ansible (see Benjamin’s talk yesterday).
Developers can generate and reproduce testing setups. Also useful for automated testing, e.g. in CI.
Convenient way to get a “snapshot” of the database for backup or further analysis.

---
Example session
$ conda create -n dsconfig -c conda-forge python=3.10 dsconfig
$ conda activate
$ json2tango --help
Usage: json2tango [options] JSONFILE
Options:
  -h, --help show this help message and exit
  -w, --write write to the Tango DB
  -u, --update don't remove things, only add/update
  -c, --case-sensitive Don't ignore the case of server, device,
...

---
Example session

---
Example session

---
Example session

---
Example session
-w flag required
for writing to DB

---
Use case: plc2tango
At MAX IV, PLC handles vacuum interlocks, cooling flows, temperatures, etc
Need to make this info available via Tango for data acquisition, GUIs, archiving…
Facade devices, a "low code" solution to create devices combining info from various parts of the control system,
configured via properties
→ Large numbers of different devices that need frequent updates.
Fortunately: naming convention!

---
Use case: plc2tango
Example: A thermocouple
B316A-O01-DIA-TCO-04
B316A = System: beamline on R3, number 16, branch A
O01 = Location: optics area 1
DIA = Subsystem: diagnostics
TCO = Equipment type: thermocouple
04 = Fourth in order
PLC tags:
B316A_O01_DIA_TCO04_AS Temperature value
B316A_O01_DIA_TCO04_BP Bypassed
B316A_O01_DIA_TCO04_A01_AA__HHInAlarm High alarm
...
Tango device name: B316A-O01/DIA/TCO-04

---
Use case: plc2tango
{
    "servers": {
        "Thermocouple": {
        "B316A-DIA": {
        "Thermocouple": {
        "B316A-O01/DIA/TCO-04": {
        "properties": {
        "AlarmsDesc": [
        "B316A_O01_DIA_TCO04_A01_AD__InAlarm:TCO channel fault"
        ],
        "AlarmsList": [
        "B316A/VAC/PLC-01/B316A_O01_DIA_TCO04_A01_AD__InAlarm"
        ],
        "AlarmsReset": [
        "False"
        ],
        "ByPassedAttribute": [
        "B316A/VAC/PLC-01/B316A_O01_DIA_TCO04_BP"
        ],
        "HighAlarmAttribute": [
        "B316A/VAC/PLC-01/B316A_O01_DIA_TCO04_A01_AA__HHInAlarm"
        ],
        "HighAlarmLevelAttribute": [
        "B316A/VAC/PLC-01/B316A_O01_DIA_TCO04_A01_AA__HHLimit"
        ],
        "HighWarningAttribute": [
        "B316A/VAC/PLC-01/B316A_O01_DIA_TCO04_A01_AA__HInAlarm"
        ], ...
Tag list (CSV file) is
parsed according to
the naming convention and turned into a dsconfig
file ->

---
Use case: plc2tango
Simple web service allows PLC engineers to upload and apply new tag lists without specific knowledge about Tango
Runs dsconfig in the background

---
Use case: Ansible
“declarative”: describe the config you want, and let the tool figure out how to get there.
“Idempotent”: do only what is needed to get to the desired state.
→ good fit for Ansible!
Our Ansible role for deploying Tango devices uses dsconfig as a python module.
(For more information about how we use Ansible at MAX IV, see Benjamin’s talk yesterday.)

---
How to get it
Code:
https://gitlab.com/MaxIV/lib-maxiv-dsconfig
PyPI:
$ pip install dsconfig
Conda:
“dsconfig” on conda-forge
RPM:
https://gitlab.com/tango-controls/RPM/dsconfig-spec

---
Rubrik Calibri Bold 32-36 p
Thanks!