## Slide 1
General SISO PID Tango Device for Temperature Control for MaxPEEM

## Slide 2
General SISO PID Tango Device for Temperature Control for MaxPEEM

## Slide 3: General SISO PID Tango Device for Temperature Control for MaxPEEM
Carla Takahashi, Áureo Freitas, Benjamin Bertrand, Mirjam Lindberg, Vincent Hardion, Darren Spruce
KITS – Software

## Slide 4: Single-Input Single-Output PID Controllers
IntroDUCTION
Overview of SISO PID controllers
KITS – Software

## Slide 5: PID controllers
SISO systems are systems that regulates only one process variable (PV), having only one input and only one actuating signal.
PID controllers are classical devices that regulates process variables according to the error between the process variable (PV) and the Setpoint (SP).
The PID calculates a actuating signal to correct the process variable according to the error, its integral and its derivative.
KITS - Software

## Slide 6: Closed Loop Control
The Closed Loop system is defined by the following equation:
The proportional term is related to the current error magnitude. It increases the speed to reach the set point, i.e. reduces the rise time, but it also increases overshoot and degrades stability.
The integral part takes into account both the magnitude and duration of the error. Thus, it reduces steady-state error and rise time, however it increases overshoot and settling time.
The derivative term, considers the slope or speed of the error over time, which decreases overshoot and settling time and may improve stability.
KITS – Software

## Slide 7: Discrete PID Controllers
In discrete systems, we have a dependency on the sampling time.
Both system transfer functions and the controller functions became dependant on the sampling frequency.
The implementation of the discrete PID device can be done using different approaches.
KITS - Software
Standard Realization
Modelling from Frequency Domain
Notes: General representation of the output u function in discrete time.
Z transform for each term of the output u
The derivative and integral term uses the Backward Euler realization for in the discrete domain
General representation of the output u function in discrete time.
𝑢[𝑘]=𝑢_𝑝 [𝑘]+𝑢_𝑖 [𝑘]+𝑢_𝑑 [𝑘]
Z transform for each term of the output u
𝑈_𝑝 [𝑧]=𝐸[𝑧] 𝑈_𝑖 [𝑧]=(𝑧^(−1) 𝑈_𝑖 [𝑧]+𝐸[𝑧] 𝑇_𝑠 )=1/((1−𝑧^(−1) ) ) 𝑇_𝑆 𝐸[𝑧]=𝑇_𝑆 𝑧/(𝑧−1) 𝐸[𝑧] 𝑈_𝑑 [𝑧]=1/𝑇_𝑠 (𝐸[𝑧]−𝑧^(−1) 𝐸[𝑧])=(1−𝑧^(−1))/𝑇_𝑠 𝐸[𝑧]=(𝑧−1)/(𝑧𝑇_𝑠 ) 𝐸[𝑧]
The derivative and integral term uses the Backward Euler realization for in the discrete domain
𝑈[𝑧]/𝐸[𝑧] =𝐾_𝑝+𝐾_𝑖 𝑇_𝑆 𝑧/(𝑧−1)+𝐾_𝑑/𝑇_𝑆 (𝑧−1)/𝑧 𝑈[𝑧]/𝐸[𝑧] =((𝐾_𝑝+𝐾_𝑖 𝑇_𝑆−𝐾_𝑑/𝑇_𝑆 ) −𝑧^(−1) (𝐾_𝑃+(2𝐾_𝑑)/𝑇_𝑠 )+𝑧^(−2) 𝐾_𝑑/𝑇_𝑆 )/(1−𝑧^(−1) )

## Slide 8: Timed Façade Devices
IntroDUCTION
Brief Explanation about TimedFacade Tango Devices
KITS – Software

## Slide 9: FacadeDevices
Façade Device
Tango FacadeDevices provide descriptive interfaces for reactive high level devices.
They are available on the git-hub repo: MaxIV-KitsControls/tango-facadedevice
Façade devices link attributes and commands from remote underlying devices.
They can also observe attribute events from remote underlying devices and forward them to user.
For this, they use specific objects create an interface between the Façade device and the remote device:
  local_attribute
  logical_attribute
  proxy_attribute
  combined_attribute
  state_attribute
  proxy_command
The rules for values and state trasitions of Façade devices are structured in a Graph.

## Slide 10: FacadeDevices
Timed Façade Device
TimedFacade Devices are based on the Facade device, but they include time handling. In this case, they can be updated periodically and execute a callback function at each update time.
The main differences are:
Name | Type | Description
UpdateTime | Polled command | This command is polled peridically, as defined in the UpdateTime polling value. It updates the Time local attriibute
Time | Local attribute | Local variable that is updated with a new timestamp at every time tick.
on_time | method | Callback function that is executed whenever the Time variable is updated

## Slide 11: SISO PID Tango Device
Implementation
Overview of the SISOPID Tango Device
KITS- Software

## Slide 12: SISO PID Device
The aim of this class is to have a software implementation of a SISO PID controller.
This device can be used for regulating non critical PV.
The control loop action is defined in the on_time method.
The UpdateTime defines the control loop frequency and the sampling rate.
KITS – Software

## Slide 13: Properties
Properties
Name | Description
Actuator | Tango attribute that will be used as the feedback actuator
ActuatorEnvelope | Actuator limits (minimum and maximum)
InterlockCondition | Tango attribute value for trigger interlock condition.
InterlockList | Tango attribute list for interlocks.
Sensor | Tango attribute that is used as feedback loop sensor.

## Slide 14: Attributes
Attributes
Name | Default value | Description
Kp | 1 | PID Proportional gain
Ki | 0 | PID Integral gain
Kd | 0 | PID Derivative gain
correcton | READ_ONLY | PID correction value (not the actuator signal)
setpoint | 0 | PV setpointvalue
home_position | 0 | Home value of the actuator to avoid saturation of the actuator.
Time | READ_ONLY | Timestamp of the last control loop action

## Slide 15: Commands
Commands
Name | Description
Start | Start control loop
Stop | Stop control loop
UpdateTime | Inherited from the TimedFacade device. Triggers the on_time callback

## Slide 16: MaxPEEM Temperature Control
Use Case
Leem2000 temperature control using the SISOPID device at MaxPEEM
KITS- Software

## Slide 17: The System
The Leem2000 is the control software of the aberration-corrected SPELEEM microscope(Elmitec GmbH) used in MaxPEEM.
In MaxPEEM, it also controls the current over a filament, which is used to change the temperature of the sample.
The measurement of the sample temperature is also available on the Leem2000.
KITS - Software

## Slide 18: Tuning Process
The sampling rate was set to 1s, which is sufficient to this temperature control system.
The method used to tune the PID was the Ziegler-Nichols approach, since we did not have a transfer function of the system.
We found the ultimate gain with
With this gain, the fundamental oscillation period was
was removed as it easily introduced instabilities.
In order to meet the system restrictions on overshoot, the was reduced.
KITS - Software

## Slide 19: PID parameters
KITS - Software
 | 3.6
 | 0
 | 40
UpdateTime | 1000 ms
 | 3.6
 | 0
 | 40
UpdateTime | 1000 ms
Overshoot | 3.3% (120 to 150℃)
Steady State Error | ±0.6℃
Controlled System

## Slide 21: General SISO PID Tango Devices and Applications
Conclusion
Our Findings and Future Work
KITS -Software

## Slide 22: Conclusions
Conclusions
A straightforward Tango based PID controller has numerous feasible applications.
The simple implementation is advantageous for tuning on the user stand point.
The current SISO PID has some room for improvement, we let our users give us some feedback about it.
A straightforward MIMO PID device would be another valuable implementation.