## Slide 1: MAX IV Archiving
Dmitry Egorov

## Slide 2: HDB++ at MAX IV
Upgrade to PostgreSQL 18+ and TimescaleDB 2.26+ is planned during the summer shutdown
Configuration using “yaml2archiving”
Interest in archiving at beamlines is growing - few beamlines have their own dashboards in Grafana to monitor the accelerator and the experiment status
Setup
One HDB++ setup (single archiver) per BL
One for accelerator (42 archivers, ~90% of data volume)
Single Postgres database cluster, 3 nodes (1 write, 2 read-only)
Separate schema for each control system
Some statistics
~ 24000 attributes
~ 3000 events per second
~ 20 control systems
~ 250 billion rows in TimescaleDB
~ 8TB disk space used (with compression)

## Slide 3: Infrastructure deployment at MAX IV

## Slide 4: Infrastructure deployment at MAX IV

## Slide 5: TimescaleDB Features

## Slide 6: Compression applied

## Slide 7: HDB deployment at MAX IV
tango_ds_hdbconfigurationmanager_timescale:
name: hdb++cm-srv
conda_env_name: hdbpp-timescale
conda_packages:
cpptango: "{{ hdbpp_cpptango_version }}"
pytango: "{{ hdbpp_pytango_version }}"
hdbpp-cm: "{{ hdbpp_cm_version }}"
hdbpp-es: "{{ hdbpp_es_version }}"
libhdbpp-timescale: "{{ libhdbpp_timescale_version }}"
instances:
- name: 1
devices:
- name: SYS/HDBPP/MANAGER-01
class: HdbConfigurationManager
properties:
ArchiverList:
- SYS/HDBPP/ARCHIVER-01
LibConfiguration:
- libname=libhdb++timescale.so
- connect_string=user=……
- logging_level=info
- log_file=true
- log_syslog=false
- log_console=false
- log_file_name=/tmp/hdb-cm-timescale.log
https://gitlab.com/MaxIV/lib-maxiv-dsconfig

## Slide 8: Configuration (yaml2archiving)
Yaml2archiving aims to ease the configuration of the HDB++ Archiving by using YAML format files in order to add/remove/update archived attributes. Each YAML file corresponds to one HdbEventSubscriber device and can include the state of the archived attributes with their settings.
db: g-v-csdb-0.maxiv.lu.se:10000
manager: sys/hdbpp/manager-01-timescale
archiver: i/mag/archiver-01-timescale
defaults:
- "../mag_defaults.yaml"
configuration:
- class: MagnetCircuit
filtering:
device:
- "i-.*"
attributes:
mainfieldcomponent:
archive_rel_change: 1.0
archive_period: 60000
polling_period: 1000
db: b-v-dummymax-csdb-0.maxiv.lu.se:10000
manager: SYS/HDBPP/MANAGER-01
archiver: SYS/HDBPP/ARCHIVER-01
configuration:
- class: TangoTest
filtering:
device: sys/tg_test/1
attributes:
double_scalar:
polling_period: 3000
archive_period: 10000
short_scalar:
polling_period: 3000
archive_period: 10000
https://gitlab.com/tango-controls/hdbpp/yaml2archiving

## Slide 9: Monitoring (ArchWizard)
"ArchWizard 🧙" is a simple web interface to the HDB++ archiving system.
It is intended for monitoring and troubleshooting, not maintenance such as adding and removing attributes.
It's built using Python, FastAPI, Jinja2 and PyTango.
https://gitlab.com/tango-controls/hdbpp/archwizard

## Slide 10: Monitoring (hdbpp-exporter)
Prometheus HDB++ exporter
An exporter is a small webserver that publishes metrics data in a text format readable by the Prometheus monitoring service.
This exporter connects to all HdbEventSubscriber devices and exports several diagnostics attributes, such as AttributeNumber, AttributeNokNumber etc.
Example output:
# HELP hdbpp_eventsubscriber_AttributeNokNumber Attribute 'AttributeNokNumber' on HdbEventSubscriber
# TYPE hdbpp_eventsubscriber_AttributeNokNumber gauge
hdbpp_eventsubscriber_AttributeNokNumber{device="SYS/HDBPP/ARCHIVER-01"} 10.0
# HELP hdbpp_eventsubscriber_AttributeNumber Attribute 'AttributeNumber' on HdbEventSubscriber
# TYPE hdbpp_eventsubscriber_AttributeNumber gauge
hdbpp_eventsubscriber_AttributeNumber{device="SYS/HDBPP/ARCHIVER-01"} 451.0
# HELP hdbpp_eventsubscriber_error_periodic_event_timeout Attribute 'AttributePendingNumber' on HdbEventSubscriber
# TYPE hdbpp_eventsubscriber_error_periodic_event_timeout gauge
hdbpp_eventsubscriber_error_periodic_event_timeout{device="SYS/HDBPP/ARCHIVER-01"} 10.0

## Slide 11: Monitoring (hdbpp-exporter)

## Slide 12: Data viewer (Archviewer)
https://gitlab.com/tango-controls/hdbpp/archviewer

## Slide 13: Data view with Grafana
SELECT
data_time AS "time",
value_r as "Beam current"
FROM att_scalar_devdouble
WHERE
$__timeFilter(data_time)
and
att_conf_id = 15713
ORDER BY 1
SELECT
data_time AS "time",
value_r as "Beam current"
FROM att_scalar_devdouble
WHERE
$__timeFilter(data_time)
and
att_conf_id = (select att_conf_id from att_conf where att_name='tango://g-v-csdb-0.maxiv.lu.se:10000/r3-319s2/dia/dcct-01/current')
ORDER BY 1

## Slide 14: Downsampling (Timebucket)
SELECT
time_bucket(‘1 min', data_time) AS time,
AVG(value_r) as "Beam current"
FROM
att_scalar_devdouble
WHERE
$__timeFilter(data_time)
and
att_conf_id = (select att_conf_id from att_conf where att_name='tango://g-v-csdb-0.maxiv.lu.se:10000/r3-319s2/dia/dcct-01/current')
GROUP BY
time
ORDER BY
time;
https://www.timescale.com/blog/simplified-time-series-analytics-using-the-time_bucket-function/

## Slide 15: Downsampling (Timebucket)

## Slide 16: Downsampling (LTTB)
SELECT
time AS "time",
value AS "Beam current"
FROM unnest((
select lttb(data_time, value_r, (($__to - $__from) / $__interval_ms)::int)
FROM att_scalar_devdouble
WHERE
$__timeFilter(data_time)
and
att_conf_id = (select att_conf_id from att_conf where att_name='tango://g-v-csdb-0.maxiv.lu.se:10000/r3-319s2/dia/dcct-01/current')
))
ORDER BY 1;
https://www.timescale.com/blog/slow-grafana-performance-learn-how-to-fix-it-using-downsampling/
https://skemman.is/bitstream/1946/15343/3/SS_MSthesis.pdf

## Slide 17: Downsampling (LTTB)

## Slide 18: Downsampling trickiness

## Slide 19: Downsampling (Continuous aggregations)
WITH conf_id AS (
SELECT att_conf_id
FROM att_conf
WHERE att_name='tango://bmn-sc-tangodb.he.jinr.ru:10000/fsd/plane0_top/adcsc_8_temp/temp_4'
),
varname AS (
SELECT 'P0-4-0/22-B' AS varname
)
SELECT
data_time AS "time",
avg_r AS varname
FROM att_scalar_devdouble_1hour
WHERE $__timeTo()::timestamp - $__timeFrom()::timestamp >= '12 hours'::interval
AND $__timeFilter(data_time)
AND att_conf_id = (SELECT att_conf_id FROM conf_id)
UNION ALL
…………
SELECT
data_time AS "time",
value_r AS varname
FROM att_scalar_devdouble
WHERE $__timeTo()::timestamp - $__timeFrom()::timestamp < '30 minutes'::interval
AND $__timeFilter(data_time)
AND att_conf_id = (SELECT att_conf_id FROM conf_id)
ORDER BY 1;
Not fully implemented at MAX IV (yet), example from another facility

## Slide 20: Downsampling (Continuous aggregations)

## Slide 21: More ways to display data
Display annotation when Heat Absorber is CLOSE

## Slide 22: More ways to display data
Display annotation when Beam Current < 350 mA